## TB3-EL-TC-30013
Consolidated Power Projects Project Details |  |  |  | Client Project Details
CPP Project Name: |  |  |  | Client Project Title:
CPP Job No: |  |  |  | Client Project Number
Bay / Cubicle / Panel Name: |  |  |  | Site Location:
CPP ITC Reference Number:
ITP Prepared by: |  |  |  | Client Checked by: | Name:
Position: |  |  |  |  | Position:
Date: |  |  |  |  | Signature:
Checked by: |  | Name: |  |  | Date:
Position:
Signature:
Date:
Tested by:
Test Commencement Date:
LINE No: | Test Category / Function |  | Acceptance Criteria |  |  | Result / Notes | Pass/Fail
1 | Wiring
2 | External connections |  | Correct and green lined as per schematics
3 | Wire labelling |  | Correct as per schematics
4 | Voltage Transformer - Phase A
5 |  |  | Matches: -Purchase Order -Schematics -Functional Design Specification
6
7
8
9
10
11 | Secondary Insulation Resistance (Core → core + core → earth, all combinations - @500VDC for 60s) |  | > 10MΩ
12 | Winding Resistance |  | < Nameplate Specification
13 | Polarity |  | P1 → P2 = S1 → S2
14 | Ratio |  | Within accuracy limits of the specified class
15 | Voltage Transformer - Phase B
16 |  |  | Matches: -Purchase Order -Schematics -Functional Design Specification
17
18
19
20
21
22 | Secondary Insulation Resistance (Core → core + core → earth, all combinations - @500VDC for 60s) |  | > 10MΩ
23 | Winding Resistance |  | < Nameplate Specification
24 | Polarity |  | P1 → P2 = S1 → S2
25 | Ratio |  | Within accuracy limits of the specified class
26 | Voltage Transformer - Phase C
27 |  |  | Matches: -Purchase Order -Schematics -Functional Design Specification
28
29
30
31
32
33 | Secondary Insulation Resistance (Core → core + core → earth, all combinations - @500VDC for 60s) |  | > 10MΩ
34 | Winding Resistance |  | < Nameplate Specification
35 | Polarity |  | P1 → P2 = S1 → S2
36 | Ratio |  | Within accuracy limits of the specified class
37 | Additional Tests
38 | PQ Sensor Ratio (if applicable)
39 | R Phase 2kV primary injection
40 | W Phase 2kV primary injection
41 | B Phase 2kV primary injection
42
43
44
45
NOTES, COMMENTS OR OTHER INFORMATION
ITP Completed (name): (CPP Project Commissioning Officer)
Signature:
Date: