## TB3-EL-TC-30001
Consolidated Power Projects Project Details |  |  |  |  | Client Project Details
CPP Project Name: |  |  |  |  | Client Project Title:
CPP Job No: |  |  |  |  | Client Project Number
Bay / Cubicle / Panel Name: |  |  |  |  | Site Location:
CPP ITC Reference Number:
ITP Prepared by: |  |  |  |  | Client Checked by: | Name:
Position: | [5 empty] | Position:
Date: | [5 empty] | Signature:
Checked by: |  | Name: |  |  |  | Date:
Position:
Signature:
Date:
Tested by:
Test Commencement Date:
LINE No: | Test Category / Function |  |  | Acceptance Criteria |  |  | Result / Notes | Pass/Fail
1 | Control cabinet
2 | External connections |  |  | Correct and green lined as per schematics
3 | AC supply |  |  | Free of short circuits
4 | Manufacturer's wiring |  |  | Matches supplied drawings
5 | Space heater(s) |  |  | Thermostat correctly set
6 | Cabinet light |  |  | Door switch works correctly
7 | Visual inspection |  |  | No apparent damage
8 | Transformer
9 |  |  |  | Matches: -Purchase Order -Functional Design Specification
10
11
12
13
14
15
16
17
18
19
20 | Oil level |  |  | As per manufacturer's recommendations
21 | Tap changer |  |  | At nominal tap unless otherwise required
22 | Insulation resistance - HV windings → earth (@5000VDC for 60s) |  |  | ≥1GΩ
23 | Insulation resistance - LV windings → earth (@500VDC for 60s) |  |  | ≥10MΩ
24 | Insulation resistance - HV windings → LV Windings (@1000VDC for 60s) |  |  | ≥1GΩ
25 | Winding resistance - HV windings |  | A-B | As per supplied FAT results
26 |  |  | B-C
27 |  |  | C-A
28 | Winding resistance - LV windings |  | A-B
29 |  |  | B-C
30 |  |  | C-A
31 | Additional Tests
32 | Ensure all Primary Connections are correct |  |  | All connections are correct. eg Neutral link connected
33
34
35
36
37
38
39
NOTES, COMMENTS OR OTHER INFORMATION
ITP Completed (name): (CPP Project Commissioning Officer)
Signature:
Date: