## TB3-EL-TC-30058
Consolidated Power Projects Project Details |  |  |  |  | Client Project Details
CPP Project Name: |  |  |  |  | Client Project Title:
CPP Job No: |  |  |  |  | Client Project Number
Bay / Cubicle / Panel Name: |  |  |  |  | Site Location:
CPP ITC Reference Number:
ITP Prepared by: |  |  |  |  | Client Checked by: | Name:
Position: | [5 empty] | Position:
Date: | [5 empty] | Signature:
Checked by: |  | Name: |  |  |  | Date:
Position:
Signature:
Date:
Tested by:
Test Commencement Date:
LINE No: | Test Category / Function |  |  | Acceptance Criteria |  |  | Result / Notes | Pass/Fail
1 | Control Cabinet
2 | External connections |  |  | Correct and green lined as per schematics
3 | Manufacturer's wiring |  |  | Matches supplied drawings
4 | AC supply |  |  | Free of short circuits
5 | DC supplies |  |  | Free of short circuits
6 | Supply polarity |  |  | Correct at all MCBs
7 | Visual inspection |  |  | No apparent damage Plumbing connected as per supplied drawings
8 | Oil / Water Separator
9 |  |  |  | Matches: -Purchase Order -Functional Design Specification
10
11
12
13
14
15 | Water drain pipe |  |  | Set such that water level peaks ~1cm below oil tank lip
16 | Water pump |  |  | Confirm pump operates in the correct direction (phase rotation)
17 | Control switch |  | Auto | Pump is activated by sump float switch
18 |  |  | Off | Pump will not be activated by sump float switch
19 |  |  | Manual | Pump operates
20 | Sump float switch |  |  | Activates pump before water reaches top of sump
21 | Bund float switch |  |  | Activates 'Bund High Level Alarm' when bund is overfull
22 | Oil tank float switch |  |  | Activates ' Oil Level High Alarm' when waste oil tank is overfull
23 | LEDs |  | Sump High Level | Illuminates when bund float switch is activated
24 |  |  | Pump Fault | Illuminates when pump AC supply is lost
25 |  |  | Waste Oil Tank High Level | Illuminates when waste oil tank float switch is activated
26 |  |  | Pump Running | Illuminates when pump is running
27 | Additional Tests
28
29
30
31
32
33
34
35
NOTES, COMMENTS OR OTHER INFORMATION
ITP Completed (name): (CPP Project Commissioning Officer)
Signature:
Date: