## TB3-EL-TC-30064
Consolidated Power Projects Project Details |  |  |  |  | Client Project Details
CPP Project Name: |  |  |  |  | Client Project Title:
CPP Job No: |  |  |  |  | Client Project Number
Bay / Cubicle / Panel Name: |  |  |  |  | Site Location:
CPP ITC Reference Number:
ITP Prepared by: |  |  |  |  | Client Checked by: | Name:
Position: | [5 empty] | Position:
Date: | [5 empty] | Signature:
Checked by: |  | Name: |  |  |  | Date:
Position:
Signature:
Date:
Tested by:
Test Commencement Date:
LINE No: | Test Category / Function |  |  | Acceptance Criteria |  |  | Result / Notes | Pass/Fail
1 |  |  |  | Matches: -Purchase Order -Functional Design Specification
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19 | Control cabinet
20 | External connections |  |  | Correct and green lined as per schematics
21 | AC supply |  |  | Free of short circuits
22 | DC supply |  |  | Free of short circuits
23 | Manufacturer's wiring |  |  | Matches supplied drawings
24 | Earthing |  |  | As per Earthing Single Line Diagram
25 | Cabinet thermostat |  |  | Set as per supplied drawings
26 | Cabinet heater |  |  | Activates when ambient temperature < thermostat minimum temperature
27 | Cabinet cooling fans |  |  | Activates when ambient temperature > thermostat minimum temperature |  |  | >45 deg
28 | Cabinet heater control switch |  | Manual | Heaters activate
29 |  |  | Off | Heaters will not be automatically activated by thermostat
30 |  |  | Auto | Heaters activated automatically by thermostat
31 | Cabinet light |  |  | Door switch works correctly
32 | Cabinet GPO |  |  | Works correctly Complies with AS (ie. Not an international socket)
33 | Visual inspection |  |  | No apparent damage
34 | Cooling System
35 | Oil temperature indicator |  | Start Fan Group 1 | Levels set as per supplied drawings
36 |  |  | Start Fan Group 2
37 |  |  | Alarm
38 |  |  | Trip
39 | HV winding temperature indicator |  | Start Fan Group 1 | Levels set as per supplied drawings
40 |  |  | Start Fan Group 2
41 |  |  | Alarm
42 |  |  | Trip
43 | MV winding temperature indicator |  | Start Fan Group 1 | Levels set as per supplied drawings
44 |  |  | Start Fan Group 2
45 |  |  | Alarm
46 |  |  | Trip
47 | Cooling fans |  |  | Correct fan is connected to each circuit
48 |  |  |  | Direction of spin is correct for all fans (phase rotation)
49 |  |  |  | Manual controls work for each fan group
50 |  |  |  | Group 1 is started by HV winding temperature gauge
51 |  |  |  | Group 1 is started by MV winding temperature gauge
52 |  |  |  | Group 1 is held on by oil temperature gauge
53 |  |  |  | Group 2 is started by HV winding temperature gauge
54 |  |  |  | Group 2 is started by MV winding temperature gauge
55 |  |  |  | Group 2 is held on by oil temperature gauge
56 | Indication LEDs |  | Fan Group 1 in Service | Illuminates when fan group 1 is running
57 |  |  | Fan Group 2 in Service | Illuminates when fan group 2 is running
58 | Fan supply voltage monitoring relay |  |  | Ensure relay does not operate due to fan startup volt drop
59 | Oil level |  |  | As per manufacturer's recommendations
60 | Oil valves |  |  | All in the service (open) position
61 | Additional Checks
62 | Bushings |  |  | Oil levels healthy No apparent damage
63 | Paintwork |  |  | No flaking or signs of rust
64
65
66
67
68
69
NOTES, COMMENTS OR OTHER INFORMATION
ITP Completed (name): (CPP Project Commissioning Officer)
Signature:
Date: