## SEL 751 Feeder Relay
Consolidated Power Projects Project Details |  |  |  |  | Client Project Details
CPP Project Name: |  |  |  |  | Client Project Title:
CPP Job No: |  |  |  |  | Client Project Number:
Bay / Cubicle / Panel Name: |  |  |  |  | Site Location:
CPP ITC Reference Number:
ITP Prepared by: |  |  |  |  | Client Checked by: |  |  | Name:
Position: | [7 empty] | Position:
Date: | [7 empty] | Signature:
Checked by: |  | Name: | [5 empty] | Date:
Position:
Signature:
Date:
Tested by:
Test Commencement Date:
LINE No: | Test Category / Function |  |  | Acceptance Criteria |  |  |  |  | Result / Notes | Pass/Fail
1 | Panel Construction
2 | Door layout and labelling |  |  | As per 'Front Panel Layout' drawing
3 | Interior layout and labelling |  |  | As per 'Back Panel Layout' drawing
4 | Panel earth |  |  | As per Earthing Single Line Diagram
5 | Fuse / MCB ratings |  |  | As per schematics
6 | Visual inspection |  |  | No apparent damage
7 | Wiring
8 | Link and terminal labels |  |  | As per schematics (Green-line)
9 | Internal panel wiring
10 | DC supplies |  |  | Free of short circuits |  |  | +ve to -ve resistance
11 |  |  |  | Individual MCB circuits are independent |  |  | 'Overload' resistance is measured between all circuits
12 |  |  |  | Correct polarity at all MCBs |  |  | As per schematics
13 | CT wiring pull test |  |  | Wire remains terminated after a firm tug |  |  | Wire remains terminated after a firm tug
14 | 'Y' Protection Relay |  |  | Acceptance criteria derived from relay manual
15 | Nameplate Details: |  |  | Matches: -Purchase Order -Functional Design Specification
16 | Part No. Serial No.
17
18
19
20 | Metering
21 | Current and voltage |  |  | Relay metering matches test set output
22 | Phase Overcurrent
23 | IDMT Pickup |  | A-B | 0.66 | x IN | ± | 0.00726
24 |  |  | B-C
25 |  |  | C-A | 0.726
26 |  |  | A-B-C
27 | High-Set Pickup |  | A-B | 7.63 | x IN | ± | 0.0763
28 |  |  | B-C
29 |  |  | C-A
30 |  |  | A-B-C
31 | Timing Characteristic |  | A-B | Expected Time |  | ± | IDMT Element 1% or 10ms (Greater of the two) High-Set Element 1% or 10ms (Greater of the two) + 30ms
32 |  |  | B-C
33 |  |  | C-A
34 |  |  | A-B-C
35 | Neutral Overcurrent
36 | IDMT Pickup |  | A-N | 0.1 | x IN | ± | 0.005
37 |  |  | B-N
38 |  |  | C-N | 0.11
39 | High-Set Pickup |  | A-N | 1.36 | x IN | ± | 0.0136
40 |  |  | B-N
41 |  |  | C-N
42 | Timing Characteristic |  | A-N | Expected Time |  | ± | IDMT Element 1% or 10ms (Greater of the two) High-Set Element 1% or 10ms (Greater of the two) + 30ms
43 |  |  | B-N
44 |  |  | C-N
45 | Neg Seq Overcurrent
46 | Neg Seq Pickup |  | 3I2 | 2 |  | ± | 0.02
47 | Neg Seq timing |  | 3I2 | Expected Time |  | ± | 1% or 10ms (Greater of the two)
48 | Circuit Breaker Fail
49 | Current Check Pickup Phase |  |  | 0.53 | x IN | ± | 0.0106
50 | Current Check Pickup Ground |  |  | 0.1 | x IN | ± | 0.01
51 | Operate Time |  |  | 200 | ms | ± | 15
52 | Other Settings
53 | Logic |  |  | Correct as per logic drawing
54 | LEDs |  |  | Correct as per logic drawing
55 | Additional Tests
56
57
58
59
60
61
62
63
NOTES, COMMENTS OR OTHER INFORMATION
ITP Completed (name): (CPP Project Commissioning Officer)
Signature:
Date: