## TB3-EL-TC-2001
Consolidated Power Projects Project Details |  |  |  |  | Client Project Details
CPP Project Name: |  |  |  |  | Client Project Title:
CPP Job No: |  |  |  |  | Client Project Number / Separable Portion / Stage
Bay / Cubicle / Panel Name: |  |  |  |  | Site Location:
Bay / Cubicle / Panel Number:
ITP Prepared by: |  |  |  |  | Client Checked by: |  |  | Name:
Position: | [7 empty] | Position:
Date: | [7 empty] | Signature:
Checked by: |  | Name: | [5 empty] | Date:
Position:
Signature:
Date:
Tested by:
Test Commencement Date:
LINE No: | Test Category / Function |  |  | Acceptance Criteria |  |  |  |  | Result / Notes | Pass/Fail (ü/û)
1 | Protection Relay |  |  | Acceptance criteria derived from relay manual |  |  |  |  | Link To Manual
| Nameplate Photo: |  |  | Matches: -Purchase Order -Functional Design Specification
Metering
| Nominal current and voltage |  |  | Relay metering matches test set output |  |  |  |  | Link to screenshot
Phase Overcurrent
| IDMT Pickup |  | A | 90 | A | ± |  |  | Link to plot
B
C
A-B-C
| High-Set Pickup |  | A | 750 | A | ±
B
C
A-B-C
| Timing Characteristic |  | A | 0.1 | s | ± | IDMT Element 5% or 20ms (Greater of the two) High-Set Element 1% or 20ms (Greater of the two) + 30ms |  | As per manufacturers curve
|  |  | B | [5 empty] | As per manufacturers curve
|  |  | C | 0.1 |  |  |  |  | As per manufacturers curve
|  |  | A-B-C | [5 empty] | As per manufacturers curve
Earth Fault Overcurrent
| IDMT Pickup |  | A | 15 | A | ±
B
C
A-B-C
| High-Set Pickup |  | A |  | A | ±
B
C
A-B-C
| Timing Characteristic |  | A | 0.00 | s | ± | IDMT Element 5% or 20ms (Greater of the two) High-Set Element 1% or 20ms (Greater of the two) + 30ms |  | As per manufacturers curve
B
C
A-B-C
| Stage 1 | Pickup | A-B-C | NA | Hz | ±
|  | Dropoff | A-B-C | NA | Hz | ±
|  | Timing | A-B-C | NA | s | ±
Circuit Breaker Fail
| Current Check Pickup Phase |  |  |  | x IN | ±
| Current Check Pickup Ground |  |  |  | x IN | ±
| Operate Time |  |  |  | ms | ±
Other Settings
| Logic |  |  | Correct as per logic drawing
| LEDs |  |  | Correct as per logic drawing
RMU
| Nameplate Photo: |  |  | Matches: -Purchase Order -Functional Design Specification
Mechanical Operations
| RMU 111-1 Disconnector OPEN / CLOSE |  |  | RMU SEMAPHORES OPERATE
| RMU 111-1 Earth Switch OPEN / CLOSE |  |  | RMU SEMAPHORES OPERATE
| RMU 112-1 Disconnector OPEN / CLOSE |  |  | RMU SEMAPHORES OPERATE
| RMU 112-1 Earth Switch OPEN / CLOSE |  |  | RMU SEMAPHORES OPERATE
| RMU 113-1 Disconnector OPEN / CLOSE |  |  | RMU SEMAPHORES OPERATE
| RMU 113-1 Earth Switch OPEN / CLOSE |  |  | RMU SEMAPHORES OPERATE
Interlock Test
| RMU 111-1 Disconnector CLOSE |  |  | RMU 111-1 Earth Switch BLOCKED
RMU 111-1 Earth Switch OPEN
| RMU 111-1 Disconnector CLOSE |  |  | RMU 111-1 Cable Cubicle BLOCKED
RMU 111-1 Earth Switch OPEN
| RMU 111-1 Disconnector OPEN |  |  | RMU 111-1 Disconnector BLOCKED
RMU 111-1 Earth Switch CLOSED
| RMU 111-1 Disconnector OPEN |  |  | RMU 111-1 Cable Cubicle OPEN
RMU 111-1 Earth Switch CLOSED
| RMU 112-1 Disconnector CLOSE |  |  | RMU 112-1 Earth Switch BLOCKED
RMU 112-1 Earth Switch OPEN
| RMU 112-1 Disconnector CLOSE |  |  | RMU 112-1 Cable Cubicle BLOCKED
RMU 112-1 Earth Switch OPEN
| RMU 112-1 Disconnector OPEN |  |  | RMU 112-1 Disconnector BLOCKED
RMU 112-1 Earth Switch CLOSED
| RMU 112-1 Disconnector OPEN |  |  | RMU 112-1 Cable Cubicle OPEN
RMU 112-1 Earth Switch CLOSED
| RMU 113-1 Disconnector CLOSE |  |  | RMU 113-1 Earth Switch BLOCKED
RMU 113-1 Earth Switch OPEN
| RMU 113-1 Disconnector CLOSE |  |  | RMU 113-1 Cable Cubicle BLOCKED
RMU 113-1 Earth Switch OPEN
| RMU 113-1 Disconnector OPEN |  |  | RMU 113-1 Disconnector BLOCKED
RMU 113-1 Earth Switch CLOSED
| RMU 113-1 Disconnector OPEN |  |  | RMU 113-1 Cable Cubicle OPEN
RMU 113-1 Earth Switch CLOSED
Ductor Testing
| RMU 111-1 - RMU 113-1 |  | L1-L1 | <10mΩ
L2-L2
L3-L3
| RMU 111-1 |  | L1-E | <10mΩ
L2-E
L3-E
| RMU 113-1 |  | L1-E | <10mΩ
L2-E
L3-E
Insulation Resistance (ALL SWITCHES CLOSED)
| RMU 11-1 MV-LV |  | MVA-LVA | >200 MΩ
MVA-LVB
MVA-LVC
MVB-LVA
MVB-LVB
MVB-LVC
MVC-LVA
MVC-LVB
MVC-LVC
| RMU 11-1 MV |  | L1-L2 | >200 MΩ
L2-L3
L3-L1
L1-E
L2-E
L3-E
| RMU 11-1 LV |  | L1-E | >200 MΩ
L2-E
L3-E
Transformer Testing
| Winding Turns Ratio Test |  | L1-L2 | [5 empty] | Link to test report
L2-L3
L3-L1
| Winding Reistance |  | L1-L2
L2-L3
L3-L1
Circuit Breaker Testing
| Circuit Breaker Timing Test | [7 empty] | Link to test report
Circuit Breaker Functional Test
Current Transformer Testing
Relay Trips via Primary injection @ 100A
Relay Trips via Primary injection @ 22.5A (EF)
NOTES, COMMENTS OR OTHER INFORMATION
ITP Completed (name): (CPP Project Commissioning Officer)
Signature:
Date: