## TB3-EL-TC-30024
Consolidated Power Projects Project Details |  |  |  | Client Project Details
CPP Project Name: |  |  |  | Client Project Title:
CPP Job No: |  |  |  | Client Project Number
Bay / Cubicle / Panel Name: |  |  |  | Site Location:
Bay / Cubicle / Panel Number:
ITP Prepared by: |  |  |  | Client Checked by: | Name:
Position: |  |  |  |  | Position:
Date: |  |  |  |  | Signature:
Checked by: |  | Name: |  |  | Date:
Position:
Signature:
Date:
Tested by:
Test Commencement Date:
LINE No: | Test Category / Function |  | Acceptance Criteria |  |  | Result / Notes | Pass/Fail
1 | Current Transformer - Phase A
2 |  |  | Matches: -Purchase Order -Schematics -Functional Design Specification -Protection Setting Report
3
4
5
6
7
8
9
10
11
12
13 | Secondary Insulation Resistance (Core → core + core → earth, all combinations - @500VDC for 60s) |  | > 10MΩ |  |  | Link to test report
14 | Winding Resistance |  | < Nameplate Specification
15 | Polarity |  | P1 → P2 = S1 → S2
16 | Magnetisation Curve |  | Vknee > Specified Iknee < Specified
17 | Ratio |  | For ratios greater than 200/1 = ±0.25% For ratios less than 200/1 = ±(50/N)% (N = Turns Ratio)
18 | DC Loop Resistance |  | For future reference |  |  | Link to test results
19 | Connected Burden @ Nominal Current |  | < Nameplate Specification |  |  | Refer To Nameplate
20 | Current Transformer - Phase B
21 |  |  | Matches: -Purchase Order -Schematics -Functional Design Specification -Protection Setting Report
22
23
24
25
26
27
28
29
30
31
32 | Secondary Insulation Resistance (Core → core + core → earth, all combinations - @500VDC for 60s) |  | > 10MΩ |  |  | Link to test report
33 | Winding Resistance |  | < Nameplate Specification
34 | Polarity |  | P1 → P2 = S1 → S2
35 | Magnetisation Curve |  | Vknee > Specified Iknee < Specified
36 | Ratio |  | For ratios greater than 200/1 = ±0.25% For ratios less than 200/1 = ±(50/N)% (N = Turns Ratio)
37 | DC Loop Resistance |  | For future reference |  |  | Link to test results
38 | Burden @ Nominal Current |  | < Nameplate Specification |  |  | Refer To Nameplate
39 | Current Transformer - Phase C
40 |  |  | Matches: -Purchase Order -Schematics -Functional Design Specification -Protection Setting Report
41
42
43
44
45
46
47
48
49
50
51 | Secondary Insulation Resistance (Core → core + core → earth, all combinations - @500VDC for 60s) |  | > 10MΩ |  |  | Link to test report
52 | Winding Resistance |  | < Nameplate Specification
53 | Polarity |  | P1 → P2 = S1 → S2
54 | Magnetisation Curve |  | Vknee > Specified Iknee < Specified
55 | Ratio |  | For ratios greater than 200/1 = ±0.25% For ratios less than 200/1 = ±(50/N)% (N = Turns Ratio)
56 | DC Loop Resistance |  | For future reference |  |  | Link to test results
57 | Burden @ Nominal Current |  | < Nameplate Specification |  |  | Refer To Nameplate
58 | Additional Tests
59
60
61
62
63
64
65
66
NOTES, COMMENTS OR OTHER INFORMATION
ITP Completed (name): (CPP Project Commissioning Officer)
Signature:
Date: