## TB3-EL-TC-30011
Consolidated Power Projects Project Details |  |  |  | Client Project Details
CPP Project Name: |  |  |  | Client Project Title:
CPP Job No: |  |  |  | Client Project Number
Bay / Cubicle / Panel Name: |  |  |  | Site Location:
Bay / Cubicle / Panel Number:
ITP Prepared by: |  |  |  | Client Checked by: | Name:
Position: |  |  |  |  | Position:
Date: |  |  |  |  | Signature:
Checked by: |  | Name: |  |  | Date:
Position:
Signature:
Date:
Tested by:
Test Commencement Date:
LINE No: | Test Category / Function |  | Acceptance Criteria |  |  | Result / Notes | Pass/Fail
1 | Control Cabinet
2 | External connections |  | Correct and green lined as per schematics
3 | AC supply |  | Free of short circuits
4 | DC supplies |  | Free of short circuits
5 | Supply polarity |  | Correct at all MCBs
6 | Space heater(s) |  | Thermostat correctly set
7 | Cabinet light |  | Door switch works correctly
8 | Visual inspection |  | No damage to insulators or control boxes
9 | Earth Switch
10 |  |  | Matches: -Purchase Order -Functional Design Specification
11
12
13
14
15
16
17
18
19
20
21 | Manual operation |  | Main contacts make / break simultaneously
22 |  |  | Auxiliary contacts operate just before end of range of motion
23 | Electrical operation |  | Initial Local control CLOSE Operation, Correct Direction and limit switch stops motor.
24 |  |  | Initial Local control OPEN Operation, Correct Direction and limit switch stops motor.
25 |  |  | Motor limit switches set correctly
26 |  |  | Achieves full range of motion
27 |  |  | Blocked by inserting manual operation handle
28 |  |  | Correct Status on HMI for Open and Close
29 |  |  | Operating Time (s)
30 |  |  | Operating Current (A)
31 | Local / remote switch |  | LOCAL / REMOTE / OFF Switch works correctly
32 |  |  | Remote Control only when switch is in REMOTE
33 |  |  | Local Control only when switch is in LOCAL
34 | Interlocking (Electrical) |  | Operations only possible when solenoid is energised (green-line interlocking circuit) - Refer to Interlocking Matrix
35 | Interlocking (Mechanical) |  | Operations only possible when associated isolators are open
36 | Lockout facility |  | Can be locked in both open and closed positions
37 | Additional Tests
38
39
40
41
42
43
44
45
NOTES, COMMENTS OR OTHER INFORMATION
ITP Completed (name): (CPP Project Commissioning Officer)
Signature:
Date: