## TB3-EL-TC-30070
Consolidated Power Projects Project Details |  |  |  |  | Client Project Details
CPP Project Name: |  |  |  |  | Client Project Title:
CPP Job No: |  |  |  |  | Client Project Number
Bay / Cubicle / Panel Name: |  |  |  |  | Site Location:
Bay / Cubicle / Panel Number:
ITP Prepared by: |  |  |  |  | Client Checked by: | Name:
Position: | [5 empty] | Position:
Date: | [5 empty] | Signature:
Checked by: |  | Name: |  |  |  | Date:
Position:
Signature:
Date:
Tested by: |  |  | Wade Nelson
Test Commencement Date: |  |  | 2026-03-12
LINE No: | Test Category / Function |  |  | Acceptance Criteria |  |  | Result / Notes | Pass/Fail
1 | Wiring
2 | Bus-wiring and external connections |  |  | Correct and green lined as per schematics
3 | High impedance buszone CT wiring |  |  | Passes 'tug' test
4 | Slide links |  |  | Do not fall open
5 | Surge Arresters
6 | A Phase Nameplate Photo: |  |  | Matches: -Purchase Order -Functional Design Specification
7
8
9
10
11
12 | DC Insulation Resistance (5kV for 60 seconds) |  |  | > 100MΩ
13 | B Phase Nameplate Photo: |  |  | Matches: -Purchase Order -Functional Design Specification
14
15
16
17
18
19 | DC Insulation Resistance (5kV for 60 seconds) |  |  | > 100MΩ
20 | C Phase Nameplate Photo: |  |  | Matches: -Purchase Order -Functional Design Specification
21
22
23
24
25
26 | DC Insulation Resistance (5kV for 60 seconds) |  |  | > 100MΩ
27 | Current Transformer - Phase A
Matches: -Purchase Order -Schematics -Functional Design Specification -Protection Setting Report
29
30
31
32
33
34
35 | Secondary Insulation Resistance (Core → core + core → earth, all combinations - @500VDC for 60s) |  |  | > 10MΩ
36 | Winding Resistance |  |  | < Nameplate Specification
37 | Polarity |  |  | P1 → P2 = S1 → S2
38 | Magnetisation Curve |  |  | Vknee > Specified Iknee < Specified
39 | Ratio |  |  | For ratios greater than 200/1 = ±0.25% For ratios less than 200/1 = ±(50/N)% (N = Turns Ratio)
40 | DC Loop Resistance |  |  | For future reference
41 | Connected Burden @ Nominal Current |  |  | < Nameplate Specification
42 | Current Transformer - Phase B
43 |  |  |  | Matches: -Purchase Order -Schematics -Functional Design Specification -Protection Setting Report
44
45
46
47
48
49
50 | Secondary Insulation Resistance (Core → core + core → earth, all combinations - @500VDC for 60s) |  |  | > 10MΩ
51 | Winding Resistance |  |  | < Nameplate Specification
52 | Polarity |  |  | P1 → P2 = S1 → S2
53 | Magnetisation Curve |  |  | Vknee > Specified Iknee < Specified
54 | Ratio |  |  | For ratios greater than 200/1 = ±0.25% For ratios less than 200/1 = ±(50/N)% (N = Turns Ratio)
55 | DC Loop Resistance |  |  | For future reference
56 | Burden @ Nominal Current |  |  | < Nameplate Specification
57 | Current Transformer - Phase C
58 |  |  |  | Matches: -Purchase Order -Schematics -Functional Design Specification -Protection Setting Report
59
60
61
62
63
64
65 | Secondary Insulation Resistance (Core → core + core → earth, all combinations - @500VDC for 60s) |  |  | > 10MΩ
66 | Winding Resistance |  |  | < Nameplate Specification
67 | Polarity |  |  | P1 → P2 = S1 → S2
68 | Magnetisation Curve |  |  | Vknee > Specified Iknee < Specified
69 | Ratio |  |  | For ratios greater than 200/1 = ±0.25% For ratios less than 200/1 = ±(50/N)% (N = Turns Ratio)
70 | DC Loop Resistance |  |  | For future reference
71 | Burden @ Nominal Current |  |  | < Nameplate Specification
72 | Circuit Breaker
73 |  |  |  | Matches: -Purchase Order -Functional Design Specification
74
75
76
77
78
79
80
81
82
83
84 | SF6 pressure is healthy |  |  | As per manufacturer's recommendations
85 | Manual spring charging |  |  | Clockwise rotation charges spring. Charged/discharged mimic works
86 | Manual operation |  |  | Operation counter ticks over Open/close mimic displays correctly in both positions
87 | Electrical operation
88 | Anti-pumping |  |  | Apply & maintain close coil voltage. Trip breaker and ensure reclose does not occur
89 | Trip Circuit 1 Opening time (3 Operations) |  |  | As per supplied manual
90 | Trip Circuit 2 Opening time (3 Operations)
91 | Closing time (3 Operations)
92 | Close-open time (2 Operations)
93 | Minimum operating voltage
94 | Spring recharge time & motor current
95 | 3-Position Switch
96 | Nameplate Photo: (See circuit breaker nameplate) |  |  | Matches: -Purchase Order -Functional Design Specification
97
98 | Manual operation |  |  | Open/closed/earthed mimic displays correctly in all positions
99 | Auxiliary Equipment
100 | Open / close switch |  |  | Open à CB Opens Close à CB Closes
101 | Local / remote switch |  |  | Local à only local commands work Remote à only remote commands work
102 | Indication lamps |  |  | CB Closed = Red CB Open = Green
103 | Interlocking
104 | Close isolator |  |  | Earth switch cannot be operated
105 | Close earth switch |  |  | Isolator cannot be operated
106 | Close circuit breaker |  |  | Isolator cannot be operated
107 |  |  |  | Earth switch cannot be operated
108 | Open isolator and leave switching handle inserted |  |  | Circuit breaker cannot be closed
109 | Close earth switch, close circuit breaker and raise cable earth lock |  |  | Circuit breaker cannot be opened
110 | Integration
111 | 'X' protection relay digital inputs |  |  | Correctly initiated from the source device as per schematic
112 | 'Y' protection relay digital inputs |  |  | Correctly initiated from the source device as per schematic
113 | Relay SCADA communications |  |  | Relays are interfacing correctly with SCADA system
114 | Additional Tests
115
116
117
118
119
120
121
122
NOTES, COMMENTS OR OTHER INFORMATION
ITP Completed (name): (CPP Project Commissioning Officer)
Signature:
Date: