## TB3-EL-TC-30014
Surge Arrester +C01 SA1 SAT
Consolidated Power Projects Project Details |  |  |  |  | Client Project Details
CPP Project Name: |  |  | Tailem Bend 3 BESS |  | Client Project Title: |  | Tailem Bend 3 BESS
CPP Job No: |  |  | 13279 |  | Client Project Number
Bay / Cubicle / Panel Name: |  |  | Surge Arrestor |  | Site Location: |  | 261 Lime Kiln Road, Tailem Bend, SA
Bay / Cubicle / Panel Number: |  |  | +C01-SA1
ITP Prepared by: |  |  | Wade Nelson |  | Client Checked by: | Name: | Andrew Pezzuto
Position: |  |  | Trainee Commissioning Officer |  |  | Position: | Senior Electrical Engineer
Date: |  |  | 2025-11-04 |  |  | Signature:
Checked by: |  | Name: | Frank Maloney |  |  | Date:
|  | Position: | Commissioning Manager
|  | Signature: | F Maloney
|  | Date: | 2025-11-04
Tested by:
Test Commencement Date:
LINE No: | Test Category / Function |  |  | Acceptance Criteria |  |  |  | Result / Notes | Pass/Fail
1 | A Phase Nameplate Photo: |  |  | Matches: -Purchase Order -Functional Design Specification
2
3
4
5
6
7 | DC Insulation Resistance (5kV for 60 seconds) |  |  | > 100MΩ
8 | Earthing |  |  | Connected to earth grid as per manufacturer's recommendation
9 | B Phase Nameplate Photo: |  |  | Matches: -Purchase Order -Functional Design Specification
10
11
12
13
14
15 | DC Insulation Resistance (5kV for 60 seconds) |  |  | > 100MΩ
16 | Earthing |  |  | Connected to earth grid as per manufacturer's recommendation
17 | C Phase Nameplate Photo: |  |  | Matches: -Purchase Order -Functional Design Specification
18
19
20
21
22
23 | DC Insulation Resistance (5kV for 60 seconds) |  |  | > 100MΩ
24 | Earthing |  |  | Connected to earth grid as per manufacturer's recommendation
25 | Additional Tests
26
27
28
29
30
31
32
33
NOTES, COMMENTS OR OTHER INFORMATION
ITP Completed (name): (CPP Project Commissioning Officer)
Signature:
Date:

## Data
ü
û
1